## Slide 1
The Big Freeze:
Wisconsin Winter of 2013-2014
Carrie Lewis, Superintendent
Milwaukee Water Works

## Slide 2: January 6, 2014

## Slide 3: Lake Michigan Percent Ice Cover 2012-2013

## Slide 4
Lake Michigan: Percent Ice Cover 2013-2014

## Slide 6: Ice Cover 1/29/14

## Slide 7
Ice
Cover
3/1/14

## Slide 8
Ice
Thickness 3/8/14

## Slide 17: Frazil Ice

## Slide 18: Significantly Reduced Pumpage
Increased discharge pressure from raw water pumps

## Slide 19: Frazil Ice on the Water Surface

## Slide 23: Propane Backup to Natural Gas
Savings of about $100,000 per year.

## Slide 24: Back-Up Power

## Slide 25: Tested During Cold Weather
All three engines started
Two radiator fans did not
X
Starting device had seized up in the cold weather
SOLUTION: Install a small heater.

## Slide 29: Distribution System
 | Dec. 1, 2012 to Mar. 31, 2013 | Dec. 1, 2013 to Mar. 31, 2014
Investigations | 3,171 | 4,091
Main Breaks | 345 | 644
Frozen Services | 0 | 154
Burst Meters | 126 | 509
Excavations | 801 | 1,093

## Slide 30: Water Main Breaks Through Sept. 30th of Each Year
Chart: 
| 2002.0 | 2003.0 | 2004.0 | 2005.0 | 2006.0 | 2007.0 | 2008.0 | 2009.0 | 2010.0 | 2011.0 | 2012.0 | 2013.0 | 2014.0
 | 719 | 483 | 538 | 537 | 370 | 608 | 436 | 507 | 314 | 465 | 357 | 454 | 857

## Slide 31: Hours Worked by Field Personnel
Chart: Weekly Hours Worked
| 2012.0 | 2013.0 | 2014.0
Jan | 36.1731 | 45.4195 | 50.0595
Feb | 39.8945 | 49.4009 | 61.6508
Mar | 49.6032 | 50.0466 | 65.2664

## Slide 32: Assistance from Contractors
 | 2013 (full year) | 2014 (to 9/30)
Water main breaks repaired by contractors | 88 repairs | 249 repairs
 | $ 1 million | $ 2.8 million
Thawing of frozen services | $ 0 | $ 400,000
Street restoration | $1.2 million | $2.2 million

## Slide 33: 1 Billion Gallons of Water Leaked

## Slide 34: Miles of Mains – By Year Constructed

## Slide 35: Main Breaks, All Years

## Slide 36: Main Breaks in Jan & Feb 2014

## Slide 41: Who thaws services?
Customer if
  Lateral is non-conductive
  Customer did not properly protect
  Customer did not follow utility advice
Utility if
  Lateral is conductive
  First thaw of season
  Utility did not provide seasonal notice

## Slide 42: 2014 PSC Decision
Preceding only applies to CUSTOMER portion of lateral
  Freeze-up of utility portion indicates poor design or construction
Utility can only request, not require, customer to run water to protect utility-owned property from damage

## Slide 44
Do it right the first time
Cross-train
Preserve expertise
Test equipment under all conditions
Know interdependencies
Have backups to backups
Lessons Re-Learned